## Sheet1
Structural Calculations for Maintenance Holes: Summary Data for 2010 MHs Standard (HS 25 Loading)
Type and H | top slab, t" | top slab, reinf req'd | Top Slab reinf req'd (BF - both ways) | bottom slab, t" | bottom slab, reinf req'd | Min soil bearing
PB or CB |  | sqin/ft, BF, both way | circular area = 0.785 square area |  | sqin/ft, TF, both way | k/sqft
MH (2010 Title)
MH 200-A-10-PB | n/a | n/a
MH 200-A-10-CB | n/a | n/a
MH 204-A-20-PB
MH 204-A-20-CB |  |  | PB = Precast Base | See Type B | See Type B | See Type B
MH 204-A-30-PB |  |  | CB = Cast in place Base
MH 204-A-30-CB
MH 204-A-40-PB |  |  | MH components per ASTM C478
MH 204-A-40-CB |  |  | Pipes per ASTM C76 (see std specs)
MH 204A |  |  | (wall =5")
MH 200-B-10-PB | 8 | 0.27 |  |  | 0.26 | 1.6
MH 200-B-10-CB | 8 | 0.27 |  |  | 0.18 | 1.12
MH 204-B-20-PB | 8 | 0.32 |  | 8 | 0.25 | 2.29
MH 204-B-20-CB | 8 | 0.32 |  | 8 | 0.17 | 1.56
MH 204-B-30-PB | 8 | 0.32 | =0.785*0.32*4.42' = 1.10 sqin | 8 | 0.31 | 2.79
MH 204-B-30-CB | 8 | 0.32 | = 1.10/0.2 = 6-#4 | 8 | 0.22 | 1.95
MH 204-B-40-PB | 8 | 0.32 |  | 8 | 0.36 | 3.26
MH 204-B-40-CB | 8 | 0.32 |  | 8 | 0.25 | 2.27
MH 204B
MH 200.5-A-10-PB | n/a | n/a
MH 200.5-A-10-CB | n/a | n/a
MH 204.5-A-20-PB
MH 204.5-A-20-CB |  |  |  | See Type B | See Type B | See Type B
MH 204.5-A-30-PB
MH 204.5-A-30-CB
MH 204.5-A-40-PB
MH 204.5-A-40-CB
MH 204.5A |  |  | (wall = 5.5")
MH 200.5-B-10-PB | 8 | 0.3 |  |  | 0.2 | 1.47
MH 200.5-B-10-CB | 8 | 0.3 |  |  | 0.15 | 1.07
MH 204.5-B-20-PB | 8 | 0.36 |  | 8 | 0.29 | 2.11
MH 204.5-B-20-CB | 8 | 0.36 |  | 8 | 0.21 | 1.53
MH 204.5-B-30-PB | 8 | 0.36 | =0.785*0.36*4.96' = 1.40 sqin | 8 | 0.36 | 2.57
MH 204.5-B-30-CB | 8 | 0.36 | = 1.40/0.2 = 7-#4 | 8 | 0.26 | 1.86
MH 204.5-B-40-PB | 8 | 0.36 |  | 8 | 0.42 | 3.04
MH 204.5-B-40-CB | 8 | 0.36 |  | 8 | 0.31 | 2.19
MH 204.5B
MH 201-A-10-PB | n/a | n/a
MH 201-A-10-CB | n/a | n/a
MH 205-A-20-PB
MH 205-A-20-CB |  |  |  | See Type B | See Type B | See Type B
MH 205-A-30-PB
MH 205-A-30-CB
MH 205-A-40-PB
MH 205-A-40-CB
MH 205A |  |  | (wall = 6")
MH 201-B-10-PB | 8 | 0.34 |  |  | 0.23 | 1.34
MH 201-B-10-CB | 8 | 0.34 |  |  | 0.17 | 1.01
MH 205-B-20-PB | 8 | 0.41 |  | 8 | 0.33 | 1.94
MH 205-B-20-CB | 8 | 0.41 |  | 8 | 0.25 | 1.45
MH 205-B-30-PB | 8 | 0.41 | =0.785*0.41*5.5' = 1.77 sqin | 8 | 0.41 | 2.4
MH 205-B-30-CB | 8 | 0.41 | = 1.77/0.2 = 9-#4 | 8 | 0.31 | 1.79
MH 205-B-40-PB | 8 | 0.41 |  | 8 | 0.47 | 2.86
MH 205-B-40-CB | 8 | 0.41 |  | 8 | 0.37 | 2.13
MH 205B
MH 202-A-10-PB | 10 | 0.35 |  |  | 0.24 | 1.28
MH 202-A-10-CB | 10 | 0.35 |  |  | 0.19 | 1.02
MH 206-A-20-PB | 10 | 0.52 |  | 10 | 0.39 | 2.08
MH 206-A-20-CB | 10 | 0.52 |  | 10 | 0.3 | 1.63
MH 206-A-30-PB | 10 | 0.52 | =0.785*0.52*6.58' = 2.68 sqin | 10 | 0.47 | 2.53
MH 206-A-30-CB | 10 | 0.52 |  | 10 | 0.37 | 1.98
MH 206-A-40-PB | 10 | 0.52 | =2.68/0.44 = 6-#6 | 10 | 0.56 | 2.98
MH 206-A-40-CB | 10 | 0.52 |  | 10 | 0.46 | 2.32
MH 206A |  |  | (wall = 7")
MH 202-B-10-PB | 8 | 0.41 |  |  | 0.24 | 1.28
MH 202-B-10-CB | 8 | 0.41 |  |  | 0.19 | 1.02
MH 206-B-20-PB | 8 | 0.5 |  | 10 | 0.29 | 1.6
MH 206-B-20-CB | 8 | 0.5 |  | 10 | 0.24 | 1.26
MH 206-B-30-PB | 8 | 0.5 | =0.785*0.50*6.58' = 2.59 sqin | 10 | 0.41 | 2.2
MH 206-B-30-CB | 8 | 0.5 | = 2.59/0.31 = 8-#5 | 10 | 0.32 | 1.72
MH 206-B-40-PB | 8 | 0.5 |  | 10 | 0.49 | 2.65
MH 206-B-40-CB | 8 | 0.5 |  | 10 | 0.41 | 2.07
MH 206B
MH 203-A-10-PB | 10 | 0.43 |  |  | 0.25 | 1.23
MH 203-A-10-CB | 10 | 0.43 |  |  | 0.21 | 1.01
MH 207-A-20-PB | 10 | 0.66 |  | 12 | 0.42 | 2.05
MH 207-A-20-CB | 10 | 0.66 |  | 12 | 0.34 | 1.66
MH 207-A-30-PB | 10 | 0.66 | =0.785*0.66*7.67' = 3.97 sqin | 12 | 0.51 | 2.49
MH 207-A-30-CB | 10 | 0.66 |  | 12 | 0.41 | 2.07
MH 207-A-40-PB | 10 | 0.66 | = 3.97/0.44 = 9-#6 | 12 | 0.6 | 2.93
MH 207-A-40-CB | 10 | 0.66 |  | 12 | 0.48 | 2.37
MH 207A |  |  | (wall = 8")
MH 203-B-10-PB | 8 | 0.49 |  |  | 0.25 | 1.23
MH 203-B-10-CB | 8 | 0.49 |  |  | 0.21 | 1.01
MH 207-B-20-PB | 8 | 0.59 |  | 12 | 0.34 | 1.63
MH 207-B-20-CB | 8 | 0.59 |  | 12 | 0.27 | 1.33
MH 207-B-30-PB | 8 | 0.59 | =0.785*0.59*7.67' = 3.55 sqin | 12 | 0.43 | 2.02
MH 207-B-30-CB | 8 | 0.59 | = 3.55/0.31 = 12-#5 | 12 | 0.35 | 1.68
MH 207-B-40-PB | 8 | 0.59 | = 3.55/0..44 = 8-#6 | 12 | 0.52 | 2.52
MH 207-B-40-CB | 8 | 0.59 |  | 12 | 0.42 | 2.04
MH 207B
MH 204-A-10-PB | 12 | 0.42 |  |  | 0.32 | 1.2
MH 204-A-10-CB | 12 | 0.42 |  |  | 0.27 | 1.01
MH 208-A-20-PB | 12 | 0.65 |  | 12 | 0.54 | 2.04
MH 208-A-20-CB | 12 | 0.65 |  | 12 | 0.45 | 1.69
MH 208-A-30-PB | 12 | 0.65 | =0.785*0.65*8.75' = 4.46 sqin | 12 | 0.66 | 2.47
MH 208-A-30-CB | 12 | 0.65 | = 4.46/0.44 = 10-#6 | 12 | 0.55 | 2.05
MH 208-A-40-PB | 12 | 0.65 |  | 12 | 0.78 | 2.91
MH 208-A-40-CB | 12 | 0.65 |  | 12 | 0.64 | 2.41
MH 208A |  |  | (wall = 9")
MH 204-B-10-PB | 10 | 0.44 |  |  | 0.32 | 1.2
MH 204-B-10-CB | 10 | 0.44 |  |  | 0.27 | 1.01
MH 2084-B-20-PB | 10 | 0.52 |  | 12 | 0.42 | 1.57
MH 208-B-20-CB | 10 | 0.52 |  | 12 | 0.35 | 1.31
MH 208-B-30-PB | 10 | 0.52 | =0.785*0.52*8.75' = 3.3.57 sqin | 12 | 0.53 | 2
MH 208-B-30-CB | 10 | 0.52 | = 3.57/0.31 = 12-#5 | 12 | 0.45 | 1.67
MH 208-B-40-PB | 10 | 0.52 |  | 12 | 0.65 | 2.41
MH 208-B-40-CB | 10 | 0.52 |  | 12 | 0.54 | 2.02
MH 208B
MH 108-A-10-PB | 12 | 0.49 |  |  | 0.39 | 1.16
MH 108-A-10-CB | 12 | 0.49 |  |  | 0.33 | 1
MH 209-A-20-PB | 12 | 0.79 |  | 14 | 0.57 | 2.04
MH 209-A-20-CB | 12 | 0.79 |  | 14 | 0.49 | 1.73
MH 209-A-30-PB | 12 | 0.79 | =0.785*0.79*9.83' = 6.10 sqin | 14 | 0.7 | 2.47
MH 209-A-30-CB | 12 | 0.79 | = 6.10/0.44 = 14-#6 | 14 | 0.59 | 2.09
MH 209-A-40-PB | 12 | 0.79 |  | 14 | 0.81 | 2.9
MH 209-A-40-CB | 12 | 0.79 |  | 14 | 0.69 | 2.46
MH 209A |  |  | (wall = 10")
MH 108-B-10-PB | 10 | 0.52 |  |  | 0.39 | 1.16
MH 108-B-10-CB | 10 | 0.52 |  |  | 0.33 | 1
MH 209-B-20-PB | 10 | 0.61 |  | 14 | 0.44 | 1.56
MH 209-B-20-CB | 10 | 0.61 |  | 14 | 0.37 | 1.33
MH 209-B-30-PB | 10 | 0.61 | =0.785*0.61*9.83' = 4.70 sqin | 14 | 0.56 | 1.99
MH 209-B-30-CB | 10 | 0.61 | = 4.70/0.31 = 15-#5 | 14 | 0.48 | 1.69
MH 209-B-40-PB | 10 | 0.61 |  | 14 | 0.68 | 2.42
MH 209-B-40-CB | 10 | 0.61 |  | 14 | 0.58 | 2.05
MH 209B
MH 205-A-10-PB | 12 | 0.57 |  |  | 0.4 | 1.16
MH 205-A-10-CB | 12 | 0.57 |  |  | 0.35 | 1.02
MH 210-A-20-PB | 12 | 0.94 |  | 14 | 0.7 | 2.02
MH 210-A-20-CB | 12 | 0.94 |  | 14 | 0.6 | 1.74
MH 210-A-30-PB | 12 | 0.94 | =0.785*0.94*10.92' = 8.06 sqin | 14 | 0.85 | 2.45
MH 210-A-30-CB | 12 | 0.94 |  | 14 | 0.73 | 2.11
MH 210-A-40-PB | 12 | 0.94 | = 7.06/0.60 = 13-#7 used | 14 | 1 | 2.87
MH 210-A-40-CB | 12 | 0.94 |  | 14 | 0.86 | 2.47
MH 210A |  |  | (wall = 11")
MH 205-B-10-PB | 10 | 0.58 |  |  | 0.4 | 1.16
MH 205-B-10-CB | 10 | 0.58 |  |  | 0.35 | 1.02
MH 210-B-20-PB | 10 | 0.68 |  | 14 | 0.52 | 1.48
MH 210-B-20-CB | 10 | 0.68 |  | 14 | 0.45 | 1.29
MH 210-B-30-PB | 10 | 0.68 | =0.785*0.68*10.92' = 5.83 sqin | 14 | 0.66 | 1.91
MH 210-B-30-CB | 10 | 0.68 | = 5.83/0.44 = 13-#6 | 14 | 0.57 | 1.65
MH 210-B-40-PB | 10 | 0.68 |  | 14 | 0.81 | 2.34
MH 210-B-40-CB | 10 | 0.68 |  | 14 | 0.7 | 2.02
MH 210B
MH 132-A-10-PB | 14 | 0.56 |  |  | 0.49 | 1.17
MH 132-A-10-CB | 14 | 0.85 |  |  | 0.43 | 1.03
MH 211-A-20-PB | 14 | 0.92 |  | 14 | 0.85 | 2.03
MH 211-A-20-CB | 14 | 0.92 |  | 14 | 0.74 | 1.77
MH 211-A-30-PB | 14 | 0.92 | =0.785*0.92*12' = 8.66 sqin | 14 | 1.02 | 2.45
MH 211-A-30-CB | 14 | 0.92 |  | 14 | 0.89 | 2.14
MH 211-A-40-PB | 14 | 0.92 | = 8.66/0.60 = 14-#7 used | 14 | 1.2 | 2.88
MH 211-A-40-CB | 14 | 0.92 |  | 14 | 1.05 | 2.51
MH 211A |  |  | (wall = 12")
MH 132-B-10-PB | 12 | 0.54 |  |  | 0.43 | 1.02
MH 132-B-10-CB | 12 | 0.54 |  |  | 0.38 | 0.9
MH 211-B-20-PB | 12 | 0.62 |  | 14 | 0.62 | 1.47
MH 211-B-20-CB | 12 | 0.62 |  | 14 | 0.54 | 1.3
MH 211-B-30-PB | 12 | 0.62 | =0.785*0.62*12' = 5.84 sqin | 14 | 0.79 | 1.9
MH 211-B-30-CB | 12 | 0.62 | = 5.84/0.44 = 13-#6 | 14 | 0.69 | 1.66
MH 211-B-40-PB | 12 | 0.62 |  | 14 | 0.97 | 2.33
MH 211-B-40-CB | 12 | 0.62 |  | 14 | 0.85 | 2.03
MH 211B
MH 206-A-10-PB | 14 | 0.64 |  |  | 0.58 | 1.27
MH 206-A-10-CB | 14 | 0.64 |  |  | 0.52 | 1.13
MH 212-A-20-PB | 14 | 1.06 |  | 15 | 1.01 | 2.2
MH 212-A-20-CB | 14 | 1.06 |  | 15 | 0.89 | 1.95
MH 212-A-30-PB | 14 | 1.06 | =0.785*1.06*13.08' = 10.89 sqin | 15 | 1.28 | 2.8
MH 212-A-30-CB | 14 | 1.06 | = 10.89/0.60 = 18-#7 | 15 | 1.13 | 2.47
MH 212-A-40-PB | 14 | 1.06 |  | 15 | 1.56 | 3.39
MH 212-A-40-CB | 14 | 1.06 |  | 15 | 1.37 | 2.99
MH 212A |  |  | (wall = 13")
MH 206-B-10-PB | 12 | 0.6 |  |  | 0.53 | 1.15
MH 206-B-10-CB | 12 | 0.6 |  |  | 0.47 | 1.03
MH 212-B-20-PB | 12 | 0.7 |  | 15 | 0.81 | 1.77
MH 212-B-20-CB | 12 | 0.7 |  | 15 | 0.72 | 1.57
MH 212-B-30-PB | 12 | 0.7 | =0.785*0.70*13.08' = 7.19 sqin | 15 | 1.09 | 2.37
MH 212-B-30-CB | 12 | 0.7 | = 7.19/0.44 = 16-#6 | 15 | 0.96 | 2.09
MH 212-B-40-PB | 12 | 0.7 |  | 15 | 1.36 | 2.96
MH 212-B-40-CB | 12 | 0.7 |  | 15 | 1.2 | 2.61
MH 212B