PROPRIETARY STORMWATER TREATMENT NOTES

Unless Otherwise Noted

- Inlet and outlet pipe must be considered CB connections per Drainage CB and Inlet Notes.

- Connections to all stormwater treatment product piping must be with shielded flexible gasketed couplings per Specification 7-17.3(2)E and 9-05.18.  Couplings must be manufactured by Indiana Seal, Joints Couplings, Romac, S

FILTERRA

- Filterra Catch Basins must be installed as shown on the approved plan. Filterra Catch Basins must be from Contech Engineered Solutions, Portland, OR (800-548-4667).

- Inlet shaping, drain rock and mulch must be as specified by the manufacturer.  Manufacturer’s inlet shaping requirements must be shown on the Drawings.

- Filterra Catch Basins underdrain must be 6” diameter MIN.  Piping within the structure must be straight. Outlet pipe must discharge to a downstream bypass CB Type 240.

- Filterra Catch Basins must be planted with a tree or shrub as shown on the approved plan.

PERK FILTER CARTRIDGES

- Perk Filter MHs, vaults or catch basins must be installed as shown on the approved plan.  Perk Filter must be from Oldcastle Stormwater Solutions, Santa Rosa, California (800-579-8819).

- Filter cartridges must be made of durable, non-corrosive, reusable polymeric and stainless steel components with no moving parts.  Filter cartridges must be installed as shown on the approved plan and either12-inch with a flow rate of 6.8 gpm or 18-inch with a flow rate of 10.2 gpm.  Cartridges may be stacked for increased treatment capacity in a vault or MH if shown on the approved plan.  Filter media must be a mixture of zeolite, perlite, and granular activated carbon (ZPC).

- Perk Filter CBs must be configured to provide pretreatment, treatment and high flow bypass in a single structure.  Perk Filter CBs must be reinforced concrete.  The inlet must be a vaned grate.  Castings, covers and grates must be ductile iron meeting the requirements of Specification 9-12.8(2).

- Perk Filter MHs must be per Specification Section 7-05.  Ring and cover access for Perk Filter MH must be per Standard Plan No. 230. Vault specifications must be submitted to Seattle Public Utilities for approval case-by-case.