PROPRIETARY STORMWATER TREATMENT NOTES

Unless Otherwise Noted

- Inlet and outlet pipe shall be considered CB connections per Drainage CB and Inlet Notes.

- Connections to all stormwater treatment product piping shall be with shielded flexible gasketed couplings per Specification 7-17.3(2)F.  Couplings shall be manufactured by Indiana Seal, Joints Couplings, Romac, Smith-Blair, Mission, Fernco or approved equal.

FILTERRA

- Filterra Catch Basins shall be installed as shown on the approved plan. Filterra Catch Basins shall be from Contech Engineered Solutions, Portland, OR (800-548-4667).

- Inlet shaping, drain rock and mulch shall be as specified by the manufacturer.  Manufacturer’s inlet shaping requirements shall be shown on the Drawings.

- Filterra Catch Basins underdrain shall be 6” diameter MIN.  Piping within the structure shall be straight. Outlet pipe shall discharge to a downstream bypass CB Type 240.

- Filterra Catch Basins shall be planted with a tree or shrub as shown on the approved plan.

PERK FILTER CARTRIDGES

- Perk Filter MHs, vaults or catch basins shall be installed as shown on the approved plan.  Perk Filter shall be from Oldcastle Stormwater Solutions, Santa Rosa, California (800-579-8819).

- Filter cartridges shall be made of durable, non-corrosive, reusable polymeric and stainless steel components with no moving parts.  Filter cartridges shall be 12-inch with a flow rate of 6.8 gpm or 18-inch with a flow rate of 10.2 gpm.  Cartridges may be stacked for increased treatment capacity in a vault or MH if shown on the approved plan.  Filter media shall be a mixture of zeolite, perlite, and granular activated carbon (ZPC).

- Perk Filter CBs shall be configured to provide pretreatment, treatment and high flow bypass in a single structure.  Perk Filter CBs shall be reinforced concrete.  The inlet shall be a vaned grate.  Castings, covers and grates shall be ductile iron meeting the requirements of Specification 9-12.8(2).

- Perk Filter MHs shall be per Specification Section 7-05.  Ring and cover access for Perk Filter MH shall be per Standard Plan No. 230. Vault specifications shall be submitted to Seattle Public Utilities for approval case-by-case.